## Revisions
Date | Rev # | Changes/Descriptions | Changes by
2013-06-26 | 0 | Create new nameplate for CGWQ & CCAQ products | SMH
2015-11-23 | 1 | Added "CGWQ-CCAQ" to file name, and added to options under Digit 14, F - Fused Disconnect (100 kA) | SMH
2019-05-16 | 2 | Added "CGWR-CCAR" to title of file because it has been in use in for a while | SMH
|  | Added Fill in Yourself Tab for CICD Dual and one for Single circuit Product | SMH
2021-10-07 | 7 | Added Jetson and Dunham Push CGWR-CCAR Pages and theis controlls in the CGWR Lookup Tables | AHC
2021-10-07 | 8 | Removed the R Series Data Sheets | AHC

## Auto Populate CGWR-CCAR
[17 empty] | Date Manufactured | 2021-10-13
[17 empty] | Serial | 4703A-02
| Model | CGWR | 0 | 75 | F - 460-3-60 | A 0 | E - ETL Listed | 1 - With valve(s) installed | 1 - Nom Flow Strainer | 0 - Std cooling 42-60F(5.6-15.6C) | D - Non-fused Disconnect | 0 - Std 5 kA | 9 - Factory enclosure | 1 - Touchscreen | 5 - Standard BACnet IP | 0 - No PWM | 1 - With Iso Pads | 1 - With Flow Swtch | 0 - Water Evap | 0 - Water Cond | 0 - No special design
| Refrigerant |  | 410A | [9 empty] | Charge | 37 lbs per circuit
| Oil Type |  | POE | [9 empty] | Unit Weight | 2005
Maximum Operating Pressures (PSIG):
| Water Side: |  |  |  | 230 |  |  |  | Condenser | [6 empty] | 464 |  |  | Chiller
| Refr. Side: |  |  |  | 650 |  |  |  | Condenser | [6 empty] | 653 |  |  | Chiller
Electrical Data:
| Rated | 460 |  |  | Volts |  |  |  | 3 |  |  | Ph |  |  | 60 |  |  |  | Hz
Model
CKT 1 | Comp. #1 |  | DSH184A4 | [5 empty] | 24.7436 |  |  | RLA |  |  | 197 |  |  |  | LRA
| Comp. #3 |  | DSH184A4 | [5 empty] | 24.7436 |  |  | RLA |  |  | 197 |  |  |  | LRA
CKT 2 | Comp. #2 |  | DSH485A4 | [5 empty] | 68 |  |  | RLA |  |  | 344 |  |  |  | LRA
| Minimum Circuit Ampacity | [14 empty] | 134.4231 |  |  | Amps
| Maximum Fuse Size | [14 empty] | 200 |  |  | Amps
| Recommended Dual-Element, | [14 empty] | 150 |  |  | Amps
Time-Delay Fuse Size
| Control Panel SCCR | [14 empty] | 5 |  |  | kA RMS
(RMS Symmetrical)
| Maximum Voltage | [14 empty] | 506 |  |  | Volts
Literature:
Installation, Operation
|  | & Maintenance Manual | [8 empty] | Controls Manual
|  | CG-SVX038A-EN | [8 empty] | CG-SVX030B-EN
Rev 1

## Auto Populate CGWR-CCAR Jetson
[17 empty] | Date Manufactured | 2021-10-13
[17 empty] | Serial | 5381A-01
| Model | CGWR | 0 | 40 | F - 460-3-60 | A 0 | E - ETL Listed | 1 - With valve(s) installed | 1 - Nom Flow Strainer | 0 - Std cooling 42-60F(5.6-15.6C) | D - Non-fused Disconnect | 0 - Std 5 kA | 0 - No enclosure | 0 - Keypad | 0 - None | 0 - No PWM | 0 - No Iso Pads | 1 - With Flow Swtch | 0 - Water Evap | 0 - Water Cond | 0 - No special design
| Refrigerant |  | 410A | [9 empty] | Charge | 24 lbs per circuit
| Oil Type |  | POE | [9 empty] | Unit Weight | 1577
Maximum Operating Pressures (PSIG):
| Water Side: |  |  |  | 230 |  |  |  | Condenser | [6 empty] | 464 |  |  | Chiller
| Refr. Side: |  |  |  | 650 |  |  |  | Condenser | [6 empty] | 653 |  |  | Chiller
Electrical Data:
| Rated | 460 |  |  | Volts |  |  |  | 3 |  |  | Ph |  |  | 60 |  |  |  | Hz
Model
CKT 1 | Comp. #1 |  | DSH120A4 | [5 empty] | 18.5897 |  |  | RLA |  |  | 142 |  |  |  | LRA
| Comp. #3 |  | DSH120A4 | [5 empty] | 18.5897 |  |  | RLA |  |  | 142 |  |  |  | LRA
CKT 2 | Comp. #2 |  | DSH240A4 | [5 empty] | 33 |  |  | RLA |  |  | 215 |  |  |  | LRA
| Minimum Circuit Ampacity | [14 empty] | 78.0449 |  |  | Amps
| Maximum Fuse Size | [14 empty] | 110 |  |  | Amps
| Recommended Dual-Element, | [14 empty] | 90 |  |  | Amps
Time-Delay Fuse Size
| Control Panel SCCR | [14 empty] | 5 |  |  | kA RMS
(RMS Symmetrical)
| Maximum Voltage | [14 empty] | 506 |  |  | Volts
Literature:
Installation, Operation
|  | & Maintenance Manual | [8 empty] | Controls Manual
|  | CG-SVX038A-EN | [8 empty] | CG-SVX030B-EN
Rev 1

## Auto Populate CGWR-CCAR DB
[17 empty] | Date Manufactured | 2021-10-13
[17 empty] | Serial | 5143A-01
[6 empty] | DB Model |  |  |  |  | W | C | S | 0 | 3 | 0 | C D |  | B | G | Q
| Model | WCCU | 0 | 40 | A - 208-3-60 | A 0 | N - No ETL listing | 0 - No WRVs | 1 - Nom Flow Strainer | 0 - Std cooling 42-60F(5.6-15.6C) | D - Non-fused Disconnect | 0 - Std 5 kA | 3 - Blankets | 0 - Keypad | 0 - None | 1 - With PWM | 0 - No Iso Pads | 1 - With Flow Swtch | 0 - Water Evap | 0 - Water Cond | 1 - With special design
| Refrigerant |  | 410A | [9 empty] | Charge | N/A
| Oil Type |  | POE | [9 empty] | Unit Weight | 0
Maximum Operating Pressures (PSIG):
| Water Side: |  |  |  | 230 |  |  |  | Condenser | [6 empty] | 464 |  |  | Chiller
| Refr. Side: |  |  |  | 650 |  |  |  | Condenser | [6 empty] | 653 |  |  | Chiller
Electrical Data:
| Rated | 208 |  |  | Volts |  |  |  | 3 |  |  | Ph |  |  | 60 |  |  |  | Hz
Model
CKT 1 | Comp. #1 |  | DSH120A3 | [5 empty] | 39.1026 |  |  | RLA |  |  | 267 |  |  |  | LRA
| Comp. #3 |  | DSH120A3 | [5 empty] | 39.1026 |  |  | RLA |  |  | 267 |  |  |  | LRA
CKT 2 | Comp. #2 |  | DSH240A3 | [5 empty] | 67 |  |  | RLA |  |  | 485 |  |  |  | LRA
| Minimum Circuit Ampacity | [14 empty] | 162.3397 |  |  | Amps
| Maximum Fuse Size | [14 empty] | 225 |  |  | Amps
| Recommended Dual-Element, | [14 empty] | 175 |  |  | Amps
Time-Delay Fuse Size
| Control Panel SCCR | [14 empty] | 5 |  |  | kA RMS
(RMS Symmetrical)
| Maximum Voltage | [14 empty] | 228.8 |  |  | Volts
Rev 1

## Auto Populate (CICD)
5kA OR 100kA?
5
Water Pressure?
[16 empty] | Date Manufactured | 2021-10-13 |  | 150
[16 empty] | Serial | 5337B-04
Model | CICD | 045 | F - 460-3-60 | A - Water Cooled Chiller | A - R-410A Scroll | 2 - Dual Circuit | 1 - Standard Efficiency | 0 - Factory Assigned | 1 - Array System | 0 - Brazed Plate | 0 - Water | 1 - Variable Flow Primary | 0 - Standard Cooling | 1 - Motorized Valves | 0 - Brazed Plate | 0 - Water
Refrigerant |  | 410A | [9 empty] | Ref Charge, lbs | Crt 1=13.5 |  |  |  |  | Crt 2=13.5
Oil Type |  | POE | [9 empty] | Unit Weight | 2040 LBS
Maximum Operating Pressures (PSIG):
Water Side: |  |  |  | 150 |  |  |  | Condenser | [6 empty] | 150 |  |  | Evaporator
Refr. Side: |  |  |  | 652 |  |  |  | Condenser | [6 empty] | 710 |  |  | Evaporator
Electrical Data:
Rated | 460 |  |  | Volts |  |  |  | 3 |  |  | Ph |  |  | 60 |  |  |  | Hz
Model
Comp 1 Circuit 1 |  | DSH240A4 | [5 empty] | 32.6923 |  |  | RLA |  |  | 215 |  |  |  | LRA
Comp 2 Circuit 2 |  | DSH240A4 | [5 empty] | 32.6923 |  |  | RLA |  |  | 215 |  |  |  | LRA
|  | NA | [5 empty] | NA |  |  | RLA |  |  | NA |  |  |  | LRA
|  | NA | [5 empty] | NA |  |  | RLA |  |  | NA |  |  |  | LRA
Minimum Circuit Ampacity | [14 empty] | 73.5577 |  |  | Amps
Maximum Fuse Size | [14 empty] | 100 |  |  | Amps
Recommended Dual-Element, | [14 empty] | 80 |  |  | Amps
Time-Delay Fuse Size
Control Panel SCCR | [14 empty] | 5 |  |  | kA RMS
(RMS Symmetrical)
Maximum Voltage | [14 empty] | 506 |  |  | Volts
Literature:
Installation, Operation
| & Maintenance Manual | [8 empty] | Controls Manual
| CG-SVX044*-EN | [8 empty] | CG-SVX030*-EN
Rev 1

## Auto Populate (FWCD)
5kA OR 100kA?
5
Water Pressure?
[16 empty] | Date Manufactured | 2021-10-13 |  | 150
[16 empty] | Serial | 5076A03
Model | FWCD | 055 | B - 230-3-60 | A - Water Cooled Chiller | A - R-410A Scroll | 2 - Dual Circuit | 1 - Standard Efficiency | 0 - Factory Assigned | 1 - Array System | 0 - Brazed Plate | 0 - Water | 0 - Constant Flow Primary | 0 - Standard Cooling | 0 - Manual Valves | 0 - Brazed Plate | 0 - Water
Refrigerant |  | 410A | [9 empty] | Ref Charge, lbs | Crt 1=15.5 |  |  |  |  | Crt 2=15.5
Oil Type |  | POE | [9 empty] | Unit Weight | 2065 LBS
Maximum Operating Pressures (PSIG):
Water Side: |  |  |  | 150 |  |  |  | Condenser | [6 empty] | 150 |  |  | Evaporator
Refr. Side: |  |  |  | 652 |  |  |  | Condenser | [6 empty] | 710 |  |  | Evaporator
Electrical Data:
Rated | 230 |  |  | Volts |  |  |  | 3 |  |  | Ph |  |  | 60 |  |  |  | Hz
Model
Comp 1 Circuit 1 |  | DSH295A3 | [5 empty] | 82.0513 |  |  | RLA |  |  | 560 |  |  |  | LRA
Comp 2 Circuit 2 |  | DSH295A3 | [5 empty] | 82.0513 |  |  | RLA |  |  | 560 |  |  |  | LRA
|  | NA | [5 empty] | NA |  |  | RLA |  |  | NA |  |  |  | LRA
|  | NA | [5 empty] | NA |  |  | RLA |  |  | NA |  |  |  | LRA
Minimum Circuit Ampacity | [14 empty] | 184.6154 |  |  | Amps
Maximum Fuse Size | [14 empty] | 250 |  |  | Amps
Recommended Dual-Element, | [14 empty] | 225 |  |  | Amps
Time-Delay Fuse Size
Control Panel SCCR | [14 empty] | 5 |  |  | kA RMS
(RMS Symmetrical)
Maximum Voltage | [14 empty] | 253 |  |  | Volts
Literature:
Installation, Operation
| & Maintenance Manual | [8 empty] | Controls Manual
Rev 1

## CICD Lookup Tables
[24 empty] | Model | Nominal Capacity | Unit Voltage | Voltage | Voltage | Unit Application | Ship with a charge? | Refr. Style | # of Circs. | # of Circs. | Efficieny/Capacity | Design Sequence | Array System | Evap HX Type | Evap Fluid Type | Evap Flow | Evap Temp Range | Evap Control Valves | Condenser HX Type | Condenser HX Type | Condenser Fluid Type | Left Blank | POWER | Water
| FWCD Model String Selection |  |  | CICD Model String Selection | [15 empty] | Weights |  |  |  | Digit 1 to 4 | Digit 5 to 7 | Digit 8 | Format #2 | Format #3 | Digit 9 |  | Digit 10 | Digit 11 | Format #1 | Digit 12 | Digit 13 | Digit 14 | Digit 15 | Digit 16 | Digit 17 | Digit 18 | Digit 19 | Digit 20 | Format #1 | Digit 21 | Digit 22 | FEED | Pressure
Digit 1 to 4 | Model = | FWCD | Digit 1 to 4 | Model = | CICD |  | Unit Size | Voltage | Comp #1 | Comp #2 | Comp #1 LRA | Comp #2 LRA | Comp #1 RLA | Comp #2 RLA | Unit MCA | Unit Max Fuse | Unit Rec. Fuse | Refr. Charge (Total) BP/S&T |  | Brazed Plate | Shell and Tube | Remote Condenser |  | CICD | 020 | A - 208-3-60 | 208 | 200-230/3/60 | A - Water Cooled Chiller | Yes | A - R-410A Scroll | 1 - Single Circuit | 1 | 1 - Standard Efficiency | 0 - Factory Assigned | 0 - Non-Array System | 0 - Brazed Plate | 0 - Water | 0 - Constant Flow Primary | 0 - Standard Cooling | 0 - Manual Valves | 0 - Brazed Plate | Brazed Plate | 0 - Water |  | 5 | 150
Digit 5 to 7 | Nominal Capacity = | 055 | Digit 5 to 7 | Nominal Capacity = | 045 |  | 020 | 200-230/3/60 | DSH120A3 | DSH120A3 | 267 | 267 | 39.1026 | 39.1026 | 87.9808 | 125 | 100 |  | 20 | 1525 | 1688 | 1320 |  | FWCD | 030 | B - 230-3-60 | 230 | 200-230/3/60 | B - Remote Condenser | No |  | 2 - Dual Circuit | 2 | 2 - High Capacity Evaporator |  | 1 - Array System |  | 2 - Ethylene Glycol | 1 - Variable Flow Primary | 1 - Standard Cooling/Ice Making | 1 - Motorized Valves | 1 - Shell and Tube | Shell and Tube | 2 - Ethylene Glycol |  | 100 | 300
Digit 8 | Unit Voltage = | B - 230-3-60 | Digit 8 | Unit Voltage = | F - 460-3-60 |  | 020 | 460/3/60 | DSH120A4 | DSH120A4 | 142 | 142 | 18.5897 | 18.5897 | 41.8269 | 60 | 50 |  | 20 | 1525 | 1688 | 1320 |  |  | 045 | F - 460-3-60 | 460 | 460/3/60 | D - Compressor Chiller w/remote Condenser | No |  |  |  | Digit 16: 3 - Propylene Glycol; Digit 18: 2 - Low Temperature Glycol Process; Digit 20: 5 - Remote Condenser | Remote Condenser | 3 - Propylene Glycol
Digit 9 | Unit Application = | A - Water Cooled Chiller | Digit 9 | Unit Application = | A - Water Cooled Chiller |  | 020 | 575/3/60 | DSH120A7 | DSH120A7 | 103 | 103 | 15.3846 | 15.3846 | 34.6154 | 50 | 40 |  | 20 | 1525 | 1688 | 1320 |  |  | 055 | G - 575-3-60 | 575 | 575/3/60 | [15 empty] | 9 - NA - Compressor Chiller
Digit 10 | Refr. Style = | A - R-410A Scroll | Digit 10 | Refr. Style = | A - R-410A Scroll |  | 030 | 200-230/3/60 | DSH184A3 | DSH184A3 | 351 | 351 | 48.0769 | 48.0769 | 108.1731 | 150 | 125 |  | 26 | 1720 | 2025 | 1320 |  |  | 065
Digit 11 | # of Circs. = | 2 - Dual Circuit | Digit 11 | # of Circs. = | 2 - Dual Circuit |  | 030 | 460/3/60 | DSH184A4 | DSH184A4 | 197 | 197 | 24.7436 | 24.7436 | 55.6731 | 80 | 60 |  | 26 | 1720 | 2025 | 1320 |  |  | 075
Digit 12 | Efficieny/Capacit = | 1 - Standard Efficiency | Digit 12 | Efficieny/Capacit = | 1 - Standard Efficiency |  | 030 | 575/3/60 | DSH184A7 | DSH184A7 | 135 | 135 | 22.4359 | 22.4359 | 50.4808 | 70 | 60 |  | 26 | 1720 | 2025 | 1320 |  |  | 085 | [19 empty] | Left Blank on purpose to stop digit 20 from spilling over
Digit 13 | Design Sequence = | 0 - Factory Assigned | Digit 13 | Design Sequence = | 0 - Factory Assigned |  | 045 | 200-230/3/60 | DSH240A3 | DSH240A3 | 485 | 485 | 67.3077 | 67.3077 | 151.4423 | 200 | 175 | 27 | 34 | 2040 | 2265 | 1550
Digit 14 | Array System = | 1 - Array System | Digit 14 | Array System = | 1 - Array System |  | 045 | 460/3/60 | DSH240A4 | DSH240A4 | 215 | 215 | 32.6923 | 32.6923 | 73.5577 | 100 | 80 | 27 | 34 | 2040 | 2265 | 1550
Digit 15 | Evap HX Type = | 0 - Brazed Plate | Digit 15 | Evap HX Type = | 0 - Brazed Plate |  | 045 | 575/3/60 | DSH240A7 | DSH240A7 | 175 | 175 | 26.2821 | 26.2821 | 59.1346 | 80 | 70 | 27 | 34 | 2040 | 2265 | 1550
Digit 16 | Evap Fluid Type = | 0 - Water | Digit 16 | Evap Fluid Type = | 0 - Water |  | 055 | 200-230/3/60 | DSH295A3 | DSH295A3 | 560 | 560 | 82.0513 | 82.0513 | 184.6154 | 250 | 225 | 31 | 42 | 2065 | 2265 | 1545
Digit 17 | Evap Flow = | 0 - Constant Flow Primary | Digit 17 | Evap Flow = | 1 - Variable Flow Primary |  | 055 | 460/3/60 | DSH295A4 | DSH295A4 | 260 | 260 | 39.7436 | 39.7436 | 89.4231 | 125 | 100 | 31 | 42 | 2065 | 2265 | 1545
Digit 18 | Evap Temp Range = | 0 - Standard Cooling | Digit 18 | Evap Temp Range = | 0 - Standard Cooling |  | 055 | 575/3/60 | DSH295A7 | DSH295A7 | 210 | 210 | 28.8462 | 28.8462 | 64.9038 | 90 | 70 | 31 | 42 | 2065 | 2265 | 1545
Digit 19 | Evap Control Valves = | 0 - Manual Valves | Digit 19 | Evap Control Valves = | 1 - Motorized Valves |  | 065 | 200-230/3/60 | DSH381A3 | DSH381A3 | 717 | 717 | 108.97 | 108.9744 | 245.1879 | 350 | 250 |  | 45 | 2565 | 3035 | 1940
Digit 20 | Condenser HX Type = | 0 - Brazed Plate | Digit 20 | Condenser HX Type = | 0 - Brazed Plate |  | 065 | 460/3/60 | DSH381A4 | DSH381A4 | 320 | 320 | 50.641 | 50.641 | 113.9423 | 150 | 125 |  | 45 | 2565 | 3035 | 1940
| Condenser Fluid Type | 0 - Water |  | Condenser Fluid Type | 0 - Water |  | 065 | 575/3/60 | DSH381A7 | DSH381A7 | 235 | 235 | 38.4615 | 38.4615 | 86.5385 | 125 | 100 |  | 45 | 2565 | 3035 | 1940
[7 empty] | 075 | 200-230/3/60 | DSH485A3 | DSH381A3 | 1010 | 717 | 121.7949 | 108.9744 | 261.2179 | 350 | 300 |  | 48 | 2570 | 3035 | 1945
[7 empty] | 075 | 460/3/60 | DSH485A4 | DSH381A4 | 344 | 320 | 67.9487 | 50.641 | 135.5769 | 200 | 150 |  | 48 | 2570 | 3035 | 1945
[7 empty] | 075 | 575/3/60 | DSH485A7 | DSH381A7 | 327 | 235 | 45.5128 | 38.4615 | 95.3526 | 125 | 110 |  | 48 | 2570 | 3035 | 1945
[7 empty] | 085 | 200-230/3/60 | DSH485A3 | DSH485A3 | 1010 | 1010 | 121.7949 | 121.7949 | 274 | 350 | 300 |  | 56 | 2860 | NA | 2152 | 1902
[7 empty] | 085 | 460/3/60 | DSH485A4 | DSH485A4 | 344 | 344 | 67.9487 | 67.9487 | 153 | 200 | 175 |  | 56 | 2860 | NA | 2152
[7 empty] | 085 | 575/3/60 | DSH485A7 | DSH485A7 | 327 | 327 | 45.5128 | 45.5128 | 102 | 125 | 125 |  | 56 | 2860 | NA | 2152
[6 empty] | SELECTED CICD UNIT | Unit Size | Voltage (Name Plate) | Comp #1 | Comp #2 | Comp #1 LRA | Comp #2 LRA | Comp #1 RLA | Comp #2 RLA | Unit MCA | Unit Max Fuse | Unit Rec. Fuse | Refr. Circ #1 | Refr. Circ. #2 | Unit Weight
[7 empty] | 045 | 460 | DSH240A4 | DSH240A4 | 215 | 215 | 32.6923 | 32.6923 | 73.5577 | 100 | 80 | 13.5 | 13.5 |  | 2040
[6 empty] | SELECTED FWCD UNIT | 055 | 230 | DSH295A3 | DSH295A3 | 560 | 560 | 82.0513 | 82.0513 | 184.6154 | 250 | 225 | 15.5 | 15.5 |  | 2065
[6 empty] | Look Up Values |  |  |  | CICD MAWP |  |  |  | FWCD MAWP | [5 empty] | Note: | These are array formulas, you must press CTRL+Shift+Enter
[5 empty] | Voltage | 460/3/60 |  |  |  | Chilled Water |  |  |  | Chilled Water
[5 empty] | Condenser HX Type | Brazed Plate |  |  |  | Cond Water |  |  |  | Cond Water
[5 empty] | # of Circiuits | 2 |  |  |  | Refr. Evap | 710 |  |  | Refr. Evap | 710
[5 empty] | Does the unit ship with a charge? | Yes |  |  |  | Refr. Cond | 652 |  |  | Refr. Cond | 652
[5 empty] | Water Cooled Condenser? | Yes
[9 empty] | # of Circs. | 1
[5 empty] | Voltage | 200-230/3/60 |  |  | Cond HX = | Brazed Plate
[5 empty] | Condenser HX Type | Brazed Plate |  |  | Unit | H20 Evap | H20 Cond | REFR. EVAP | REFR. COND
[5 empty] | # of Circiuits | 2 |  |  |  | MAWP | MAWP | MAWP | MAWP
[5 empty] | Does the unit ship with a charge? | Yes |  |  | 20 Tons
[5 empty] | Water Cooled Condenser? | Yes |  |  | 30 Tons | 400 | 400 | 725 | 725
[9 empty] | 45 Tons | 400 | 400 | 725 | 725
[9 empty] | 55 Tons | 400 | 400 | 725 | 725
[9 empty] | 65 Tons | 400 | 400 | 725 | 725
[9 empty] | 75 Tons | 400 | 400 | 725 | 725
[9 empty] | # of Circs. | 2
[9 empty] | Cond HX = | Brazed Plate
[9 empty] | Unit | H20 Evap | H20 Cond | REFR. EVAP | REFR. COND
[10 empty] | MAWP | MAWP | MAWP | MAWP
20 Tons
[9 empty] | 30 Tons | 333 | 362 | 710 | 652
[9 empty] | 45 Tons | 333 | 362 | 710 | 652
[9 empty] | 55 Tons | 333 | 362 | 710 | 652
[9 empty] | 65 Tons | 333 | 362 | 710 | 652
[9 empty] | 75 Tons | 333 | 362 | 710 | 652
[9 empty] | # of Circs. | 2
[9 empty] | Cond HX = | Shell and Tube
[9 empty] | Unit | H20 Evap | H20 Cond | REFR. EVAP | REFR. COND
[10 empty] | MAWP | MAWP | MAWP | MAWP
020
[9 empty] | 030 | 333 | 300 | - | 600
[9 empty] | 045 | 333 | 180 | - | 650
[9 empty] | 055 | 333 | 180 | - | 650
[9 empty] | 065 | 333 | 180 | - | 650
[9 empty] | 075 | 333 | 180 | - | 650

## CGWR Look Up Tables
CGWR-CCAR Model String Selection Trane
Digit 1 to 4 | Model = | CGWR |  |  | Unit Size | Voltage | Comp #1 | Comp #3 | Comp #2 | Comp #1 LRA | Comp #3 LRA | Comp #2 LRA | Comp #1 RLA | Comp #3 RLA | Comp #2 RLA | Unit MCA | Unit Max Fuse | Unit Rec. Fuse |  | Unit Series | Tons | Refrigerant Charge | Operating weight | Condenser Water psi | Unit |  |  | Design Sequence | Agency | Water | Evaporator Wye | Evap Temp | Power | Short Circuit Rating | Sound | Local Unit Controller | Communication | Power | Neoprene Isolator | Flow | Evap Fluid | Cond Fluid | Special Design
Digit 5 to 7 | Nominal Capacity = | 075 |  |  | 15 | 200-230/3/60 | DSH90A3 | DSH90A3 |  | 203 | 203 |  | 27.5641 | 27.5641 |  | 62.0192 | 80 | 70 |  | CGWR | 20 | 25 lbs | 1042 | 250 | Series | Tons | Unit Voltage | Factory assigned | Listing | Regulating Valves | Strainer | Range | Connection | (SCCR) | Enclosure | Interface | Options | Monitor | Pads | Switch | type | type | Features 0 = None, 1 = Yes
Digit 8 | Unit Voltage = | F - 460-3-60 |  |  | 15 | 460/3/60 | DSH90A4 | DSH90A4 |  | 98 | 98 |  | 14.1026 | 14.1026 |  | 31.7308 | 45 | 35 |  | CGWR | 30 | 37 lbs | 1242 | 230 | CGWR | 20 | A - 208-3-60 | A 0 | N - No ETL listing | 0 - No WRVs | 0 - No Strainer | 0 - Std cooling 42-60F(5.6-15.6C) | T - Std Terminal Block | 0 - Std 5 kA | 0 - No enclosure | 0 - Keypad | 0 - None | 0 - No PWM | 0 - No Iso Pads | 0 - No Flow Swtch | 0 - Water Evap | 0 - Water Cond | 0 - No special design
Digit 9 to 10 | Design Sequence = | A 0 |  |  | 15 | 575/3/60 | DSH90A7 | DSH90A7 |  | 84 | 84 |  | 11.5385 | 11.5385 |  | 25.9615 | 35 | 30 |  | CGWR | 40 | 24 lbs per circuit | 1577 | 230 | CCAR | 30 | B - 230-3-60 |  | E - ETL Listed | 1 - With valve(s) installed | 1 - Nom Flow Strainer | 1 - Std cooling/ice 20-60F(-6.7-15.6C) | D - Non-fused Disconnect | 1 - Opt 100 kA | 3 - Blankets | 1 - Touchscreen | 2 - LonTalk | 1 - With PWM | 1 - With Iso Pads | 1 - With Flow Swtch | 2 - EG Evap | 2 - EG Cond | 1 - With special design
Digit 11 | Agency Listing = | E - ETL Listed |  |  | 20 | 200-230/3/60 | DSH120A3 | DSH120A3 |  | 267 | 267 |  | 39.1026 | 39.1026 |  | 87.9808 | 125 | 100 |  | CGWR | 50 | 29 lbs per circuit | 1833 | 230 | WCCU | 40 | F - 460-3-60 |  |  |  | 2 - Strainer w/Kit |  | F - Fused Disconnect |  | 9 - Factory enclosure |  | 4 - BACnet MS/TP |  |  |  | 3 - PG Evap | 3 - PG Cond
Digit 12 | Condenser WRV = | 1 - With valve(s) installed | Look Up Values Trane |  | 20 | 460/3/60 | DSH120A4 | DSH120A4 |  | 142 | 142 |  | 18.5897 | 18.5897 |  | 41.8269 | 60 | 50 |  | CGWR | 65 | 32 lbs per circuit | 2005 | 230 | NWCR | 50 | G - 575-3-60 | [9 empty] | 5 - Standard BACnet IP |  |  |  | 4 - Methanol | 4 - Methanol
Digit 13 | Evap Wye Strainer = | 1 - Nom Flow Strainer | CGWR |  | 20 | 575/3/60 | DSH120A7 | DSH120A7 |  | 103 | 103 |  | 15.3846 | 15.3846 |  | 34.6154 | 50 | 40 |  | CGWR | 75 | 37 lbs per circuit | 2005 | 230 |  | 65 | [10 empty] | 6 - Standard Modbus |  |  |  |  | 9 - CCAR
Digit 14 | Evap Temp Range = | 0 - Std cooling 42-60F(5.6-15.6C) | 75 |  | 30 | 200-230/3/60 | DSH184A3 | DSH184A3 |  | 351 | 351 |  | 48.0769 | 48.0769 |  | 108.1731 | 150 | 125 |  | CCAR | 20 | N/A | 732 | N/A |  | 75 | [10 empty] | 8 - Johnson N2
Digit 15 | Power Connection = | D - Non-fused Disconnect | F - 460-3-60 |  | 30 | 460/3/60 | DSH184A4 | DSH184A4 |  | 197 | 197 |  | 24.7436 | 24.7436 |  | 55.6731 | 80 | 60 |  | CCAR | 30 | N/A | 809 | N/A
Digit 16 | Short Circuit Rating = | 0 - Std 5 kA | 460 |  | 30 | 575/3/60 | DSH184A7 | DSH184A7 |  | 135 | 135 |  | 22.4359 | 22.4359 |  | 50.4808 | 70 | 60 |  | CCAR | 40 | N/A | 1110 | N/A
Digit 17 | Sound Attenuation = | 9 - Factory enclosure |  |  | 40 | 200-230/3/60 | DSH120A3 | DSH120A3 | DSH240A3 | 267 | 267 | 485 | 39.1026 | 39.1026 | 67 | 162.3397 | 225 | 175 |  | CCAR | 50 | N/A | 1152 | N/A
Digit 18 | Control Interfece = | 1 - Touchscreen | Look Up Values Jetson |  | 40 | 460/3/60 | DSH120A4 | DSH120A4 | DSH240A4 | 142 | 142 | 215 | 18.5897 | 18.5897 | 33 | 78.0449 | 110 | 90 |  | CCAR | 65 | N/A | 1336 | N/A
Digit 19 | Remote BMS = | 5 - Standard BACnet IP | CGWR |  | 40 | 575/3/60 | DSH120A7 | DSH120A7 | DSH240A7 | 103 | 103 | 175 | 15.3846 | 15.3846 | 26 | 63.6218 | 80 | 70 |  | CCAR | 75 | N/A | 2005 | N/A
Digit 20 | Power Monitor = | 0 - No PWM | 40 |  | 50 | 200-230/3/60 | DSH140A3 | DSH140A3 | DSH295A3 | 304 | 304 | 560 | 41.0256 | 41.0256 | 82 | 184.6154 | 250 | 225 |  | WCCU | 20 | N/A |  | 250
Digit 21 | Neoprene Isolators = | 1 - With Iso Pads | F - 460-3-60 |  | 50 | 460/3/60 | DSH140A4 | DSH140A4 | DSH295A4 | 147 | 147 | 260 | 19.2308 | 19.2308 | 40 | 88.141 | 125 | 100 |  | WCCU | 30 | N/A |  | 230
Digit 22 | Flow Switch = | 1 - With Flow Swtch | 460 |  | 50 | 575/3/60 | DSH140A7 | DSH140A7 | DSH295A7 | 122 | 122 | 210 | 16.6667 | 16.6667 | 29 | 69.391 | 90 | 80 |  | WCCU | 40 | N/A |  | 230
Digit 23 | Evap Fluid Type = | 0 - Water Evap |  |  | 65 | 200-230/3/60 | DSH184A3 | DSH184A3 | DSH381A3 | 351 | 351 | 717 | 48.0769 | 48.0769 | 109 | 232.3718 | 300 | 250 |  | WCCU | 50 | N/A |  | 230 | A - 208-3-60 | 200-230/3/60 | 208
Digit 24 | Cond Fluid Type = | 0 - Water Cond | Look Up Values DB |  | 65 | 460/3/60 | DSH184A4 | DSH184A4 | DSH381A4 | 197 | 197 | 320 | 24.7436 | 24.7436 | 51 | 112.7885 | 150 | 125 |  | WCCU | 65 | N/A |  | 230 | B - 230-3-60 | 200-230/3/60 | 230
Digit 25 | Special Options = | 0 - No special design | WCCU |  | 65 | 575/3/60 | DSH184A7 | DSH184A7 | DSH381A7 | 135 | 135 | 235 | 22.4359 | 22.4359 | 38 | 92.9487 | 125 | 110 |  | WCCU | 75 | N/A |  | 230 | F - 460-3-60 | 460/3/60 | 460
|  |  | 40 |  | 75 | 200-230/3/60 | DSH184A3 | DSH184A3 | DSH485A3 | 351 | 351 | 1010 | 48.0769 | 48.0769 | 122 | 248.3974 | 350 | 300 |  | NWCR | 20 |  |  | 250 | G - 575-3-60 | 575/3/60 | 575
| CGWR-CCAR Model String Selection Jetson |  | A - 208-3-60 |  | 75 | 460/3/60 | DSH184A4 | DSH184A4 | DSH485A4 | 197 | 197 | 344 | 24.7436 | 24.7436 | 68 | 134.4231 | 200 | 150 |  | NWCR | 30 |  |  | 230
Digit 1 to 4 | Model = | CGWR | 208 |  | 75 | 575/3/60 | DSH184A7 | DSH184A7 | DSH485A7 | 135 | 135 | 327 | 22.4359 | 22.4359 | 46 | 101.7628 | 125 | 110 |  | NWCR | 40 |  |  | 230
Digit 5 to 7 | Nominal Capacity = | 040 | [17 empty] | NWCR | 50 |  |  | 230
Digit 8 | Unit Voltage = | F - 460-3-60 | [17 empty] | NWCR | 65 |  |  | 230
Digit 9 to 10 | Design Sequence = | A 0 | [17 empty] | NWCR | 75 |  |  | 230
Digit 11 | Agency Listing = | E - ETL Listed
Digit 12 | Condenser WRV = | 1 - With valve(s) installed | SELECTED UNIT | Unit Type | Unit Size | Voltage (Name Plate) | Comp #1 | Comp #3 | Comp #2 | Comp #1 LRA | Comp #3 LRA | Comp #2 LRA | Comp #1 RLA | Comp #3 RLA | Comp #2 RLA | Unit MCA | Unit Max Fuse | Unit Rec. Fuse | Refrigerant Charge | Operating Weight | Condenser Water psi
Digit 13 | Evap Wye Strainer = | 1 - Nom Flow Strainer |  | CGWR | 75 | 460/3/60 | DSH184A4 | DSH184A4 | DSH485A4 | 197 | 197 | 344 | 24.7436 | 24.7436 | 68 | 134.4231 | 200 | 150 | 37 lbs per circuit | 2005 | 230
Digit 14 | Evap Temp Range = | 0 - Std cooling 42-60F(5.6-15.6C) |  | CGWR | 40 | 460/3/60 | DSH120A4 | DSH120A4 | DSH240A4 | 142 | 142 | 215 | 18.5897 | 18.5897 | 33 | 78.0449 | 110 | 90 | 24 lbs per circuit | 1577 | 230
Digit 15 | Power Connection = | D - Non-fused Disconnect |  | WCCU | 40 | 200-230/3/60 | DSH120A3 | DSH120A3 | DSH240A3 | 267 | 267 | 485 | 39.1026 | 39.1026 | 67 | 162.3397 | 225 | 175 | N/A | 0 | 230
Digit 16 | Short Circuit Rating = | 0 - Std 5 kA
Digit 17 | Sound Attenuation = | 0 - No enclosure | [13 empty] | Note | These are array formulas, you must press CTRL+Shift+Enter
Digit 18 | Control Interfece = | 0 - Keypad
Digit 19 | Remote BMS = | 0 - None
Digit 20 | Power Monitor = | 0 - No PWM
Digit 21 | Neoprene Isolators = | 0 - No Iso Pads
Digit 22 | Flow Switch = | 1 - With Flow Swtch
Digit 23 | Evap Fluid Type = | 0 - Water Evap
Digit 24 | Cond Fluid Type = | 0 - Water Cond
Digit 25 | Special Options = | 0 - No special design
CGWR-CCAR Model String Selection DB
Digit 1 to 4 | Model = | WCCU
Digit 5 to 7 | Nominal Capacity = | 040
Digit 8 | Unit Voltage = | A - 208-3-60
Digit 9 to 10 | Design Sequence = | A 0
Digit 11 | Agency Listing = | N - No ETL listing
Digit 12 | Condenser WRV = | 0 - No WRVs
Digit 13 | Evap Wye Strainer = | 1 - Nom Flow Strainer
Digit 14 | Evap Temp Range = | 0 - Std cooling 42-60F(5.6-15.6C)
Digit 15 | Power Connection = | D - Non-fused Disconnect
Digit 16 | Short Circuit Rating = | 0 - Std 5 kA
Digit 17 | Sound Attenuation = | 3 - Blankets
Digit 18 | Control Interfece = | 0 - Keypad
Digit 19 | Remote BMS = | 0 - None
Digit 20 | Power Monitor = | 1 - With PWM
Digit 21 | Neoprene Isolators = | 0 - No Iso Pads
Digit 22 | Flow Switch = | 1 - With Flow Swtch
Digit 23 | Evap Fluid Type = | 0 - Water Evap
Digit 24 | Cond Fluid Type = | 0 - Water Cond
Digit 25 | Special Options = | 1 - With special design