## Revisions
Date | Rev # | Changes/Descriptions | Changes by
2013-06-26 | 0 | Create new nameplate for CGWQ & CCAQ products | SMH
2015-11-23 | 1 | Added "CGWQ-CCAQ" to file name, and added to options under Digit 14, F - Fused Disconnect (100 kA) | SMH
2019-05-16 | 2 | Added "CGWR-CCAR" to title of file because it has been in use in for a while | SMH
|  | Added Fill in Yourself Tab for CICD Dual and one for Single circuit Product | SMH
2021-10-07 | 7 | Added Jetson and Dunham Push CGWR-CCAR Pages and theis controlls in the CGWR Lookup Tables | AHC
2021-10-07 | 8 | Removed the R Series Data Sheets | AHC
2021-10-13 | 9 | Adding ACCA Look Up Table | AHC

## Auto Populate CGWR-CCAR
[17 empty] | Date Manufactured | 2021-11-29
[17 empty] | Serial | 4972A-01
| Model | CGWR | 0 | 65 | A - 208-3-60 | A 0 | E - ETL Listed | 1 - With valve(s) installed | 1 - Nom Flow Strainer | 0 - Std cooling 42-60F(5.6-15.6C) | D - Non-fused Disconnect | 0 - Std 5 kA | 9 - Factory enclosure | 1 - Touchscreen | 4 - BACnet MS/TP | 1 - With PWM | 1 - With Iso Pads | 1 - With Flow Swtch | 0 - Water Evap | 0 - Water Cond | 0 - No special design
| Refrigerant |  | 410A | [9 empty] | Charge | 32 lbs per circuit
| Oil Type |  | POE | [9 empty] | Unit Weight | 2005
Maximum Operating Pressures (PSIG):
| Water Side: |  |  |  | 230 |  |  |  | Condenser | [6 empty] | 464 |  |  | Chiller
| Refr. Side: |  |  |  | 650 |  |  |  | Condenser | [6 empty] | 653 |  |  | Chiller
Electrical Data:
| Rated | 208 |  |  | Volts |  |  |  | 3 |  |  | Ph |  |  | 60 |  |  |  | Hz
Model
CKT 1 | Comp. #1 |  | DSH184A3 | [5 empty] | 48.0769 |  |  | RLA |  |  | 351 |  |  |  | LRA
| Comp. #3 |  | DSH184A3 | [5 empty] | 48.0769 |  |  | RLA |  |  | 351 |  |  |  | LRA
CKT 2 | Comp. #2 |  | DSH381A3 | [5 empty] | 109 |  |  | RLA |  |  | 717 |  |  |  | LRA
| Minimum Circuit Ampacity | [14 empty] | 232.3718 |  |  | Amps
| Maximum Fuse Size | [14 empty] | 300 |  |  | Amps
| Recommended Dual-Element, | [14 empty] | 250 |  |  | Amps
Time-Delay Fuse Size
| Control Panel SCCR | [14 empty] | 5 |  |  | kA RMS
(RMS Symmetrical)
| Maximum Voltage | [14 empty] | 228.8 |  |  | Volts
Literature:
Installation, Operation
|  | & Maintenance Manual | [8 empty] | Controls Manual
|  | CG-SVX038A-EN | [8 empty] | CG-SVX030B-EN
Rev 1

## Auto Populate CGWR-CCAR Jetson
[17 empty] | Date Manufactured | 2021-11-29
[17 empty] | Serial | 5381A-01
| Model | CGWR | 0 | 40 | F - 460-3-60 | A 0 | E - ETL Listed | 1 - With valve(s) installed | 1 - Nom Flow Strainer | 0 - Std cooling 42-60F(5.6-15.6C) | D - Non-fused Disconnect | 0 - Std 5 kA | 0 - No enclosure | 0 - Keypad | 0 - None | 0 - No PWM | 0 - No Iso Pads | 1 - With Flow Swtch | 0 - Water Evap | 0 - Water Cond | 0 - No special design
| Refrigerant |  | 410A | [9 empty] | Charge | 24 lbs per circuit
| Oil Type |  | POE | [9 empty] | Unit Weight | 1577
Maximum Operating Pressures (PSIG):
| Water Side: |  |  |  | 230 |  |  |  | Condenser | [6 empty] | 464 |  |  | Chiller
| Refr. Side: |  |  |  | 650 |  |  |  | Condenser | [6 empty] | 653 |  |  | Chiller
Electrical Data:
| Rated | 460 |  |  | Volts |  |  |  | 3 |  |  | Ph |  |  | 60 |  |  |  | Hz
Model
CKT 1 | Comp. #1 |  | DSH120A4 | [5 empty] | 18.5897 |  |  | RLA |  |  | 142 |  |  |  | LRA
| Comp. #3 |  | DSH120A4 | [5 empty] | 18.5897 |  |  | RLA |  |  | 142 |  |  |  | LRA
CKT 2 | Comp. #2 |  | DSH240A4 | [5 empty] | 33 |  |  | RLA |  |  | 215 |  |  |  | LRA
| Minimum Circuit Ampacity | [14 empty] | 78.0449 |  |  | Amps
| Maximum Fuse Size | [14 empty] | 110 |  |  | Amps
| Recommended Dual-Element, | [14 empty] | 90 |  |  | Amps
Time-Delay Fuse Size
| Control Panel SCCR | [14 empty] | 5 |  |  | kA RMS
(RMS Symmetrical)
| Maximum Voltage | [14 empty] | 506 |  |  | Volts
Literature:
Installation, Operation
|  | & Maintenance Manual | [8 empty] | Controls Manual
|  | CG-SVX038A-EN | [8 empty] | CG-SVX030B-EN
Rev 1

## Auto Populate CGWR-CCAR DB
[17 empty] | Date Manufactured | 2021-11-29
[17 empty] | Serial | 5152A-01
[6 empty] | DB Model |  |  |  |  | W | C | S | 0 | 5 | 0 | A R |  | B | G | Q
| Model | WCCU | 0 | 50 | F - 460-3-60 | A 0 | N - No ETL listing | 1 - With valve(s) installed | 0 - No Strainer | 0 - Std cooling 42-60F(5.6-15.6C) | T - Std Terminal Block | 0 - Std 5 kA | 0 - No enclosure | 0 - Keypad | 4 - BACnet MS/TP | 1 - With PWM | 0 - No Iso Pads | 1 - With Flow Swtch | 0 - Water Evap | 0 - Water Cond | 1 - With special design
| Refrigerant |  | 410A | [9 empty] | Charge | N/A
| Oil Type |  | POE | [9 empty] | Unit Weight | 0
Maximum Operating Pressures (PSIG):
| Water Side: |  |  |  | 230 |  |  |  | Condenser | [6 empty] | 464 |  |  | Chiller
| Refr. Side: |  |  |  | 650 |  |  |  | Condenser | [6 empty] | 653 |  |  | Chiller
Electrical Data:
| Rated | 460 |  |  | Volts |  |  |  | 3 |  |  | Ph |  |  | 60 |  |  |  | Hz
Model
CKT 1 | Comp. #1 |  | DSH140A4 | [5 empty] | 19.2308 |  |  | RLA |  |  | 147 |  |  |  | LRA
| Comp. #3 |  | DSH140A4 | [5 empty] | 19.2308 |  |  | RLA |  |  | 147 |  |  |  | LRA
CKT 2 | Comp. #2 |  | DSH295A4 | [5 empty] | 40 |  |  | RLA |  |  | 260 |  |  |  | LRA
| Minimum Circuit Ampacity | [14 empty] | 88.141 |  |  | Amps
| Maximum Fuse Size | [14 empty] | 125 |  |  | Amps
| Recommended Dual-Element, | [14 empty] | 100 |  |  | Amps
Time-Delay Fuse Size
| Control Panel SCCR | [14 empty] | 5 |  |  | kA RMS
(RMS Symmetrical)
| Maximum Voltage | [14 empty] | 506 |  |  | Volts
Rev 1

## Auto Populate (CICD)
5kA OR 100kA?
5
Water Pressure?
[16 empty] | Date Manufactured | 2021-11-29 |  | 150
[16 empty] | Serial | 5315A-01
Model | CICD | 055 | F - 460-3-60 | B - Remote Condenser | A - R-410A Scroll | 2 - Dual Circuit | 1 - Standard Efficiency | 0 - Factory Assigned | 0 - Non-Array System | 0 - Brazed Plate | 0 - Water | 0 - Constant Flow Primary | 0 - Standard Cooling | 0 - Manual Valves | 5 - Remote Condenser | 0 - Water
Refrigerant |  | 410A | [9 empty] | Ref Charge, lbs | Crt 1=NA |  |  |  |  | Crt 2=NA
Oil Type |  | POE | [9 empty] | Unit Weight | 1545 LBS
Maximum Operating Pressures (PSIG):
Water Side: |  |  |  | N/A |  |  |  | Condenser | [6 empty] | 150 |  |  | Evaporator
Refr. Side: |  |  |  | N/A |  |  |  | Condenser | [6 empty] | 710 |  |  | Evaporator
Electrical Data:
Rated | 460 |  |  | Volts |  |  |  | 3 |  |  | Ph |  |  | 60 |  |  |  | Hz
Model
Comp 1 Circuit 1 |  | DSH295A4 | [5 empty] | 39.7436 |  |  | RLA |  |  | 260 |  |  |  | LRA
Comp 2 Circuit 2 |  | DSH295A4 | [5 empty] | 39.7436 |  |  | RLA |  |  | 260 |  |  |  | LRA
|  | NA | [5 empty] | NA |  |  | RLA |  |  | NA |  |  |  | LRA
|  | NA | [5 empty] | NA |  |  | RLA |  |  | NA |  |  |  | LRA
Minimum Circuit Ampacity | [14 empty] | 89.4231 |  |  | Amps
Maximum Fuse Size | [14 empty] | 125 |  |  | Amps
Recommended Dual-Element, | [14 empty] | 100 |  |  | Amps
Time-Delay Fuse Size
Control Panel SCCR | [14 empty] | 5 |  |  | kA RMS
(RMS Symmetrical)
Maximum Voltage | [14 empty] | 506 |  |  | Volts
Literature:
Installation, Operation
| & Maintenance Manual | [8 empty] | Controls Manual
| CG-SVX044*-EN | [8 empty] | CG-SVX030*-EN
Rev 1

## Auto Populate (FWCD)
5kA OR 100kA?
5
Water Pressure?
[16 empty] | Date Manufactured | 2021-11-29 |  | 150
[16 empty] | Serial | 5076A03
Model | FWCD | 055 | B - 230-3-60 | A - Water Cooled Chiller | A - R-410A Scroll | 2 - Dual Circuit | 1 - Standard Efficiency | 0 - Factory Assigned | 1 - Array System | 0 - Brazed Plate | 0 - Water | 0 - Constant Flow Primary | 0 - Standard Cooling | 0 - Manual Valves | 0 - Brazed Plate | 0 - Water
Refrigerant |  | 410A | [9 empty] | Ref Charge, lbs | Crt 1=15.5 |  |  |  |  | Crt 2=15.5
Oil Type |  | POE | [9 empty] | Unit Weight | 2065 LBS
Maximum Operating Pressures (PSIG):
Water Side: |  |  |  | 150 |  |  |  | Condenser | [6 empty] | 150 |  |  | Evaporator
Refr. Side: |  |  |  | 652 |  |  |  | Condenser | [6 empty] | 710 |  |  | Evaporator
Electrical Data:
Rated | 230 |  |  | Volts |  |  |  | 3 |  |  | Ph |  |  | 60 |  |  |  | Hz
Model
Comp 1 Circuit 1 |  | DSH295A3 | [5 empty] | 82.0513 |  |  | RLA |  |  | 560 |  |  |  | LRA
Comp 2 Circuit 2 |  | DSH295A3 | [5 empty] | 82.0513 |  |  | RLA |  |  | 560 |  |  |  | LRA
|  | NA | [5 empty] | NA |  |  | RLA |  |  | NA |  |  |  | LRA
|  | NA | [5 empty] | NA |  |  | RLA |  |  | NA |  |  |  | LRA
Minimum Circuit Ampacity | [14 empty] | 184.6154 |  |  | Amps
Maximum Fuse Size | [14 empty] | 250 |  |  | Amps
Recommended Dual-Element, | [14 empty] | 225 |  |  | Amps
Time-Delay Fuse Size
Control Panel SCCR | [14 empty] | 5 |  |  | kA RMS
(RMS Symmetrical)
Maximum Voltage | [14 empty] | 253 |  |  | Volts
Literature:
Installation, Operation
| & Maintenance Manual | [8 empty] | Controls Manual
Rev 1

## CGWR Look Up Tables
CGWR-CCAR Model String Selection Trane
Digit 1 to 4 | Model = | CGWR |  |  | Unit Size | Voltage | Comp #1 | Comp #3 | Comp #2 | Comp #1 LRA | Comp #3 LRA | Comp #2 LRA | Comp #1 RLA | Comp #3 RLA | Comp #2 RLA | Unit MCA | Unit Max Fuse | Unit Rec. Fuse |  | Unit Series | Tons | Refrigerant Charge | Operating weight | Condenser Water psi | Unit |  |  | Design Sequence | Agency | Water | Evaporator Wye | Evap Temp | Power | Short Circuit Rating | Sound | Local Unit Controller | Communication | Power | Neoprene Isolator | Flow | Evap Fluid | Cond Fluid | Special Design
Digit 5 to 7 | Nominal Capacity = | 065 |  |  | 15 | 200-230/3/60 | DSH90A3 | DSH90A3 |  | 203 | 203 |  | 27.5641 | 27.5641 |  | 62.0192 | 80 | 70 |  | CGWR | 20 | 25 lbs | 1042 | 250 | Series | Tons | Unit Voltage | Factory assigned | Listing | Regulating Valves | Strainer | Range | Connection | (SCCR) | Enclosure | Interface | Options | Monitor | Pads | Switch | type | type | Features 0 = None, 1 = Yes
Digit 8 | Unit Voltage = | A - 208-3-60 |  |  | 15 | 460/3/60 | DSH90A4 | DSH90A4 |  | 98 | 98 |  | 14.1026 | 14.1026 |  | 31.7308 | 45 | 35 |  | CGWR | 30 | 37 lbs | 1242 | 230 | CGWR | 20 | A - 208-3-60 | A 0 | N - No ETL listing | 0 - No WRVs | 0 - No Strainer | 0 - Std cooling 42-60F(5.6-15.6C) | T - Std Terminal Block | 0 - Std 5 kA | 0 - No enclosure | 0 - Keypad | 0 - None | 0 - No PWM | 0 - No Iso Pads | 0 - No Flow Swtch | 0 - Water Evap | 0 - Water Cond | 0 - No special design
Digit 9 to 10 | Design Sequence = | A 0 |  |  | 15 | 575/3/60 | DSH90A7 | DSH90A7 |  | 84 | 84 |  | 11.5385 | 11.5385 |  | 25.9615 | 35 | 30 |  | CGWR | 40 | 24 lbs per circuit | 1577 | 230 | CCAR | 30 | B - 230-3-60 |  | E - ETL Listed | 1 - With valve(s) installed | 1 - Nom Flow Strainer | 1 - Std cooling/ice 20-60F(-6.7-15.6C) | D - Non-fused Disconnect | 1 - Opt 100 kA | 3 - Blankets | 1 - Touchscreen | 2 - LonTalk | 1 - With PWM | 1 - With Iso Pads | 1 - With Flow Swtch | 2 - EG Evap | 2 - EG Cond | 1 - With special design
Digit 11 | Agency Listing = | E - ETL Listed |  |  | 20 | 200-230/3/60 | DSH120A3 | DSH120A3 |  | 267 | 267 |  | 39.1026 | 39.1026 |  | 87.9808 | 125 | 100 |  | CGWR | 50 | 29 lbs per circuit | 1833 | 230 | WCCU | 40 | F - 460-3-60 |  |  |  | 2 - Strainer w/Kit |  | F - Fused Disconnect |  | 9 - Factory enclosure |  | 4 - BACnet MS/TP |  |  |  | 3 - PG Evap | 3 - PG Cond
Digit 12 | Condenser WRV = | 1 - With valve(s) installed | Look Up Values Trane |  | 20 | 460/3/60 | DSH120A4 | DSH120A4 |  | 142 | 142 |  | 18.5897 | 18.5897 |  | 41.8269 | 60 | 50 |  | CGWR | 65 | 32 lbs per circuit | 2005 | 230 | NWCR | 50 | G - 575-3-60 | [9 empty] | 5 - Standard BACnet IP |  |  |  | 4 - Methanol | 4 - Methanol
Digit 13 | Evap Wye Strainer = | 1 - Nom Flow Strainer | CGWR |  | 20 | 575/3/60 | DSH120A7 | DSH120A7 |  | 103 | 103 |  | 15.3846 | 15.3846 |  | 34.6154 | 50 | 40 |  | CGWR | 75 | 37 lbs per circuit | 2005 | 230 |  | 65 | [10 empty] | 6 - Standard Modbus |  |  |  |  | 9 - CCAR
Digit 14 | Evap Temp Range = | 0 - Std cooling 42-60F(5.6-15.6C) | 65 |  | 30 | 200-230/3/60 | DSH184A3 | DSH184A3 |  | 351 | 351 |  | 48.0769 | 48.0769 |  | 108.1731 | 150 | 125 |  | CCAR | 20 | N/A | 732 | N/A |  | 75 | [10 empty] | 8 - Johnson N2
Digit 15 | Power Connection = | D - Non-fused Disconnect | A - 208-3-60 |  | 30 | 460/3/60 | DSH184A4 | DSH184A4 |  | 197 | 197 |  | 24.7436 | 24.7436 |  | 55.6731 | 80 | 60 |  | CCAR | 30 | N/A | 809 | N/A
Digit 16 | Short Circuit Rating = | 0 - Std 5 kA | 208 |  | 30 | 575/3/60 | DSH184A7 | DSH184A7 |  | 135 | 135 |  | 22.4359 | 22.4359 |  | 50.4808 | 70 | 60 |  | CCAR | 40 | N/A | 1110 | N/A
Digit 17 | Sound Attenuation = | 9 - Factory enclosure |  |  | 40 | 200-230/3/60 | DSH120A3 | DSH120A3 | DSH240A3 | 267 | 267 | 485 | 39.1026 | 39.1026 | 67 | 162.3397 | 225 | 175 |  | CCAR | 50 | N/A | 1152 | N/A
Digit 18 | Control Interfece = | 1 - Touchscreen | Look Up Values Jetson |  | 40 | 460/3/60 | DSH120A4 | DSH120A4 | DSH240A4 | 142 | 142 | 215 | 18.5897 | 18.5897 | 33 | 78.0449 | 110 | 90 |  | CCAR | 65 | N/A | 1336 | N/A
Digit 19 | Remote BMS = | 4 - BACnet MS/TP | CGWR |  | 40 | 575/3/60 | DSH120A7 | DSH120A7 | DSH240A7 | 103 | 103 | 175 | 15.3846 | 15.3846 | 26 | 63.6218 | 80 | 70 |  | CCAR | 75 | N/A | 2005 | N/A
Digit 20 | Power Monitor = | 1 - With PWM | 40 |  | 50 | 200-230/3/60 | DSH140A3 | DSH140A3 | DSH295A3 | 304 | 304 | 560 | 41.0256 | 41.0256 | 82 | 184.6154 | 250 | 225 |  | WCCU | 20 | N/A |  | 250
Digit 21 | Neoprene Isolators = | 1 - With Iso Pads | F - 460-3-60 |  | 50 | 460/3/60 | DSH140A4 | DSH140A4 | DSH295A4 | 147 | 147 | 260 | 19.2308 | 19.2308 | 40 | 88.141 | 125 | 100 |  | WCCU | 30 | N/A |  | 230
Digit 22 | Flow Switch = | 1 - With Flow Swtch | 460 |  | 50 | 575/3/60 | DSH140A7 | DSH140A7 | DSH295A7 | 122 | 122 | 210 | 16.6667 | 16.6667 | 29 | 69.391 | 90 | 80 |  | WCCU | 40 | N/A |  | 230
Digit 23 | Evap Fluid Type = | 0 - Water Evap |  |  | 65 | 200-230/3/60 | DSH184A3 | DSH184A3 | DSH381A3 | 351 | 351 | 717 | 48.0769 | 48.0769 | 109 | 232.3718 | 300 | 250 |  | WCCU | 50 | N/A |  | 230 | A - 208-3-60 | 200-230/3/60 | 208
Digit 24 | Cond Fluid Type = | 0 - Water Cond | Look Up Values DB |  | 65 | 460/3/60 | DSH184A4 | DSH184A4 | DSH381A4 | 197 | 197 | 320 | 24.7436 | 24.7436 | 51 | 112.7885 | 150 | 125 |  | WCCU | 65 | N/A |  | 230 | B - 230-3-60 | 200-230/3/60 | 230
Digit 25 | Special Options = | 0 - No special design | WCCU |  | 65 | 575/3/60 | DSH184A7 | DSH184A7 | DSH381A7 | 135 | 135 | 235 | 22.4359 | 22.4359 | 38 | 92.9487 | 125 | 110 |  | WCCU | 75 | N/A |  | 230 | F - 460-3-60 | 460/3/60 | 460
|  |  | 50 |  | 75 | 200-230/3/60 | DSH184A3 | DSH184A3 | DSH485A3 | 351 | 351 | 1010 | 48.0769 | 48.0769 | 122 | 248.3974 | 350 | 300 |  | NWCR | 20 |  |  | 250 | G - 575-3-60 | 575/3/60 | 575
| CGWR-CCAR Model String Selection Jetson |  | F - 460-3-60 |  | 75 | 460/3/60 | DSH184A4 | DSH184A4 | DSH485A4 | 197 | 197 | 344 | 24.7436 | 24.7436 | 68 | 134.4231 | 200 | 150 |  | NWCR | 30 |  |  | 230
Digit 1 to 4 | Model = | CGWR | 460 |  | 75 | 575/3/60 | DSH184A7 | DSH184A7 | DSH485A7 | 135 | 135 | 327 | 22.4359 | 22.4359 | 46 | 101.7628 | 125 | 110 |  | NWCR | 40 |  |  | 230
Digit 5 to 7 | Nominal Capacity = | 040 | [17 empty] | NWCR | 50 |  |  | 230
Digit 8 | Unit Voltage = | F - 460-3-60 | [17 empty] | NWCR | 65 |  |  | 230
Digit 9 to 10 | Design Sequence = | A 0 | [17 empty] | NWCR | 75 |  |  | 230
Digit 11 | Agency Listing = | E - ETL Listed
Digit 12 | Condenser WRV = | 1 - With valve(s) installed | SELECTED UNIT | Unit Type | Unit Size | Voltage (Name Plate) | Comp #1 | Comp #3 | Comp #2 | Comp #1 LRA | Comp #3 LRA | Comp #2 LRA | Comp #1 RLA | Comp #3 RLA | Comp #2 RLA | Unit MCA | Unit Max Fuse | Unit Rec. Fuse | Refrigerant Charge | Operating Weight | Condenser Water psi
Digit 13 | Evap Wye Strainer = | 1 - Nom Flow Strainer |  | CGWR | 65 | 200-230/3/60 | DSH184A3 | DSH184A3 | DSH381A3 | 351 | 351 | 717 | 48.0769 | 48.0769 | 109 | 232.3718 | 300 | 250 | 32 lbs per circuit | 2005 | 230
Digit 14 | Evap Temp Range = | 0 - Std cooling 42-60F(5.6-15.6C) |  | CGWR | 40 | 460/3/60 | DSH120A4 | DSH120A4 | DSH240A4 | 142 | 142 | 215 | 18.5897 | 18.5897 | 33 | 78.0449 | 110 | 90 | 24 lbs per circuit | 1577 | 230
Digit 15 | Power Connection = | D - Non-fused Disconnect |  | WCCU | 50 | 460/3/60 | DSH140A4 | DSH140A4 | DSH295A4 | 147 | 147 | 260 | 19.2308 | 19.2308 | 40 | 88.141 | 125 | 100 | N/A | 0 | 230
Digit 16 | Short Circuit Rating = | 0 - Std 5 kA
Digit 17 | Sound Attenuation = | 0 - No enclosure | [13 empty] | Note | These are array formulas, you must press CTRL+Shift+Enter
Digit 18 | Control Interfece = | 0 - Keypad
Digit 19 | Remote BMS = | 0 - None
Digit 20 | Power Monitor = | 0 - No PWM
Digit 21 | Neoprene Isolators = | 0 - No Iso Pads
Digit 22 | Flow Switch = | 1 - With Flow Swtch
Digit 23 | Evap Fluid Type = | 0 - Water Evap
Digit 24 | Cond Fluid Type = | 0 - Water Cond
Digit 25 | Special Options = | 0 - No special design
CGWR-CCAR Model String Selection DB
Digit 1 to 4 | Model = | WCCU
Digit 5 to 7 | Nominal Capacity = | 050
Digit 8 | Unit Voltage = | F - 460-3-60
Digit 9 to 10 | Design Sequence = | A 0
Digit 11 | Agency Listing = | N - No ETL listing
Digit 12 | Condenser WRV = | 1 - With valve(s) installed
Digit 13 | Evap Wye Strainer = | 0 - No Strainer
Digit 14 | Evap Temp Range = | 0 - Std cooling 42-60F(5.6-15.6C)
Digit 15 | Power Connection = | T - Std Terminal Block
Digit 16 | Short Circuit Rating = | 0 - Std 5 kA
Digit 17 | Sound Attenuation = | 0 - No enclosure
Digit 18 | Control Interfece = | 0 - Keypad
Digit 19 | Remote BMS = | 4 - BACnet MS/TP
Digit 20 | Power Monitor = | 1 - With PWM
Digit 21 | Neoprene Isolators = | 0 - No Iso Pads
Digit 22 | Flow Switch = | 1 - With Flow Swtch
Digit 23 | Evap Fluid Type = | 0 - Water Evap
Digit 24 | Cond Fluid Type = | 0 - Water Cond
Digit 25 | Special Options = | 1 - With special design

## CICD Lookup Tables
[22 empty] | Model | Nominal Capacity | Unit Voltage | Voltage | Voltage | Unit Application | Ship with a charge? | Refr. Style | # of Circs. | # of Circs. | Efficieny/Capacity | Design Sequence | Array System | Evap HX Type | Evap Fluid Type | Evap Flow | Evap Temp Range | Evap Control Valves | Condenser HX Type | Condenser HX Type | Condenser Fluid Type | Left Blank | POWER | Water
| FWCD Model String Selection | [16 empty] | Weights |  |  |  | Digit 1 to 4 | Digit 5 to 7 | Digit 8 | Format #2 | Format #3 | Digit 9 |  | Digit 10 | Digit 11 | Format #1 | Digit 12 | Digit 13 | Digit 14 | Digit 15 | Digit 16 | Digit 17 | Digit 18 | Digit 19 | Digit 20 | Format #1 | Digit 21 | Digit 22 | FEED | Pressure
Digit 1 to 4 | Model = | FWCD |  |  | Unit Size | Voltage | Comp #1 | Comp #2 | Comp #1 LRA | Comp #2 LRA | Comp #1 RLA | Comp #2 RLA | Unit MCA | Unit Max Fuse | Unit Rec. Fuse | Refr. Charge (Total) BP/S&T |  | Brazed Plate | Shell and Tube | Remote Condenser |  | CICD | 020 | A - 208-3-60 | 208 | 200-230/3/60 | A - Water Cooled Chiller | Yes | A - R-410A Scroll | 1 - Single Circuit | 1 | 1 - Standard Efficiency | 0 - Factory Assigned | 0 - Non-Array System | 0 - Brazed Plate | 0 - Water | 0 - Constant Flow Primary | 0 - Standard Cooling | 0 - Manual Valves | 0 - Brazed Plate | Brazed Plate | 0 - Water |  | 5 | 150
Digit 5 to 7 | Nominal Capacity = | 055 |  |  | 020 | 200-230/3/60 | DSH120A3 | DSH120A3 | 267 | 267 | 39.1026 | 39.1026 | 87.9808 | 125 | 100 |  | 20 | 1525 | 1688 | 1320 |  | FWCD | 030 | B - 230-3-60 | 230 | 200-230/3/60 | B - Remote Condenser | No |  | 2 - Dual Circuit | 2 | 2 - High Capacity Evaporator |  | 1 - Array System |  | 2 - Ethylene Glycol | 1 - Variable Flow Primary | 1 - Standard Cooling/Ice Making | 1 - Motorized Valves | 1 - Shell and Tube | Shell and Tube | 2 - Ethylene Glycol |  | 100 | 300
Digit 8 | Unit Voltage = | B - 230-3-60 |  |  | 020 | 460/3/60 | DSH120A4 | DSH120A4 | 142 | 142 | 18.5897 | 18.5897 | 41.8269 | 60 | 50 |  | 20 | 1525 | 1688 | 1320 |  |  | 045 | F - 460-3-60 | 460 | 460/3/60 | D - Compressor Chiller w/remote Condenser | No |  |  |  | Digit 16: 3 - Propylene Glycol; Digit 18: 2 - Low Temperature Glycol Process; Digit 20: 5 - Remote Condenser | Remote Condenser | 3 - Propylene Glycol
Digit 9 | Unit Application = | A - Water Cooled Chiller |  |  | 020 | 575/3/60 | DSH120A7 | DSH120A7 | 103 | 103 | 15.3846 | 15.3846 | 34.6154 | 50 | 40 |  | 20 | 1525 | 1688 | 1320 |  |  | 055 | G - 575-3-60 | 575 | 575/3/60 | [15 empty] | 9 - NA - Compressor Chiller
Digit 10 | Refr. Style = | A - R-410A Scroll |  |  | 030 | 200-230/3/60 | DSH184A3 | DSH184A3 | 351 | 351 | 48.0769 | 48.0769 | 108.1731 | 150 | 125 |  | 26 | 1720 | 2025 | 1320 |  |  | 065
Digit 11 | # of Circs. = | 2 - Dual Circuit |  |  | 030 | 460/3/60 | DSH184A4 | DSH184A4 | 197 | 197 | 24.7436 | 24.7436 | 55.6731 | 80 | 60 |  | 26 | 1720 | 2025 | 1320 |  |  | 075
Digit 12 | Efficieny/Capacit = | 1 - Standard Efficiency |  |  | 030 | 575/3/60 | DSH184A7 | DSH184A7 | 135 | 135 | 22.4359 | 22.4359 | 50.4808 | 70 | 60 |  | 26 | 1720 | 2025 | 1320 |  |  | 085 | [19 empty] | Left Blank on purpose to stop digit 20 from spilling over
Digit 13 | Design Sequence = | 0 - Factory Assigned |  |  | 045 | 200-230/3/60 | DSH240A3 | DSH240A3 | 485 | 485 | 67.3077 | 67.3077 | 151.4423 | 200 | 175 | 27 | 34 | 2040 | 2265 | 1550
Digit 14 | Array System = | 1 - Array System |  |  | 045 | 460/3/60 | DSH240A4 | DSH240A4 | 215 | 215 | 32.6923 | 32.6923 | 73.5577 | 100 | 80 | 27 | 34 | 2040 | 2265 | 1550
Digit 15 | Evap HX Type = | 0 - Brazed Plate |  |  | 045 | 575/3/60 | DSH240A7 | DSH240A7 | 175 | 175 | 26.2821 | 26.2821 | 59.1346 | 80 | 70 | 27 | 34 | 2040 | 2265 | 1550
Digit 16 | Evap Fluid Type = | 0 - Water |  |  | 055 | 200-230/3/60 | DSH295A3 | DSH295A3 | 560 | 560 | 82.0513 | 82.0513 | 184.6154 | 250 | 225 | 31 | 42 | 2065 | 2265 | 1545
Digit 17 | Evap Flow = | 0 - Constant Flow Primary |  |  | 055 | 460/3/60 | DSH295A4 | DSH295A4 | 260 | 260 | 39.7436 | 39.7436 | 89.4231 | 125 | 100 | 31 | 42 | 2065 | 2265 | 1545
Digit 18 | Evap Temp Range = | 0 - Standard Cooling |  |  | 055 | 575/3/60 | DSH295A7 | DSH295A7 | 210 | 210 | 28.8462 | 28.8462 | 64.9038 | 90 | 70 | 31 | 42 | 2065 | 2265 | 1545
Digit 19 | Evap Control Valves = | 0 - Manual Valves |  |  | 065 | 200-230/3/60 | DSH381A3 | DSH381A3 | 717 | 717 | 108.97 | 108.9744 | 245.1879 | 350 | 250 |  | 45 | 2565 | 3035 | 1940
Digit 20 | Condenser HX Type = | 0 - Brazed Plate |  |  | 065 | 460/3/60 | DSH381A4 | DSH381A4 | 320 | 320 | 50.641 | 50.641 | 113.9423 | 150 | 125 |  | 45 | 2565 | 3035 | 1940
Digit 21 | Condenser Fluid Type | 0 - Water |  |  | 065 | 575/3/60 | DSH381A7 | DSH381A7 | 235 | 235 | 38.4615 | 38.4615 | 86.5385 | 125 | 100 |  | 45 | 2565 | 3035 | 1940
[5 empty] | 075 | 200-230/3/60 | DSH485A3 | DSH381A3 | 1010 | 717 | 121.7949 | 108.9744 | 261.2179 | 350 | 300 |  | 48 | 2570 | 3035 | 1945
[5 empty] | 075 | 460/3/60 | DSH485A4 | DSH381A4 | 344 | 320 | 67.9487 | 50.641 | 135.5769 | 200 | 150 |  | 48 | 2570 | 3035 | 1945
| CICD Model String Selection |  |  |  | 075 | 575/3/60 | DSH485A7 | DSH381A7 | 327 | 235 | 45.5128 | 38.4615 | 95.3526 | 125 | 110 |  | 48 | 2570 | 3035 | 1945
Digit 1 to 4 | Model = | CICD |  |  | 085 | 200-230/3/60 | DSH485A3 | DSH485A3 | 1010 | 1010 | 121.7949 | 121.7949 | 274 | 350 | 300 |  | 56 | 2860 | NA | 2152 | 1902
Digit 5 to 7 | Nominal Capacity = | 055 |  |  | 085 | 460/3/60 | DSH485A4 | DSH485A4 | 344 | 344 | 67.9487 | 67.9487 | 153 | 200 | 175 |  | 56 | 2860 | NA | 2152
Digit 8 | Unit Voltage = | F - 460-3-60 |  |  | 085 | 575/3/60 | DSH485A7 | DSH485A7 | 327 | 327 | 45.5128 | 45.5128 | 102 | 125 | 125 |  | 56 | 2860 | NA | 2152
Digit 9 | Unit Application = | B - Remote Condenser
Digit 10 | Refr. Style = | A - R-410A Scroll |  | SELECTED CICD UNIT | Unit Size | Voltage (Name Plate) | Comp #1 | Comp #2 | Comp #1 LRA | Comp #2 LRA | Comp #1 RLA | Comp #2 RLA | Unit MCA | Unit Max Fuse | Unit Rec. Fuse | Refr. Circ #1 | Refr. Circ. #2 | Unit Weight
Digit 11 | # of Circs. = | 2 - Dual Circuit |  |  | 055 | 460 | DSH295A4 | DSH295A4 | 260 | 260 | 39.7436 | 39.7436 | 89.4231 | 125 | 100 | NA | NA |  | 1545
Digit 12 | Efficieny/Capacit = | 1 - Standard Efficiency |  | SELECTED FWCD UNIT | 055 | 230 | DSH295A3 | DSH295A3 | 560 | 560 | 82.0513 | 82.0513 | 184.6154 | 250 | 225 | 15.5 | 15.5 |  | 2065
Digit 13 | Design Sequence = | 0 - Factory Assigned
Digit 14 | Array System = | 0 - Non-Array System |  | Look Up Values |  |  |  | CICD MAWP |  |  |  | FWCD MAWP | [5 empty] | Note: | These are array formulas, you must press CTRL+Shift+Enter
Digit 15 | Evap HX Type = | 0 - Brazed Plate | Voltage | 460/3/60 |  |  |  | Chilled Water |  |  |  | Chilled Water
Digit 16 | Evap Fluid Type = | 0 - Water | Condenser HX Type | Remote Condenser |  |  |  | Cond Water |  |  |  | Cond Water
Digit 17 | Evap Flow = | 0 - Constant Flow Primary | # of Circiuits | 2 |  |  |  | Refr. Evap | 710 |  |  | Refr. Evap | 710
Digit 18 | Evap Temp Range = | 0 - Standard Cooling | Does the unit ship with a charge? | No |  |  |  | Refr. Cond | NA |  |  | Refr. Cond | 652
Digit 19 | Evap Control Valves = | 0 - Manual Valves | Water Cooled Condenser? | No
Digit 20 | Condenser HX Type = | 5 - Remote Condenser |  |  |  |  | # of Circs. | 1
Digit 21 | Condenser Fluid Type | 0 - Water | Voltage | 200-230/3/60 |  |  | Cond HX = | Brazed Plate
|  |  | Condenser HX Type | Brazed Plate |  |  | Unit | H20 Evap | H20 Cond | REFR. EVAP | REFR. COND
|  |  | # of Circiuits | 2 |  |  |  | MAWP | MAWP | MAWP | MAWP
|  |  | Does the unit ship with a charge? | Yes |  |  | 20 Tons
|  |  | Water Cooled Condenser? | Yes |  |  | 30 Tons | 400 | 400 | 725 | 725
[7 empty] | 45 Tons | 400 | 400 | 725 | 725
[7 empty] | 55 Tons | 400 | 400 | 725 | 725
[7 empty] | 65 Tons | 400 | 400 | 725 | 725
[7 empty] | 75 Tons | 400 | 400 | 725 | 725
[7 empty] | # of Circs. | 2
[7 empty] | Cond HX = | Brazed Plate
[7 empty] | Unit | H20 Evap | H20 Cond | REFR. EVAP | REFR. COND
[8 empty] | MAWP | MAWP | MAWP | MAWP
20 Tons
[7 empty] | 30 Tons | 333 | 362 | 710 | 652
[7 empty] | 45 Tons | 333 | 362 | 710 | 652
[7 empty] | 55 Tons | 333 | 362 | 710 | 652
[7 empty] | 65 Tons | 333 | 362 | 710 | 652
[7 empty] | 75 Tons | 333 | 362 | 710 | 652
[7 empty] | # of Circs. | 2
[7 empty] | Cond HX = | Shell and Tube
[7 empty] | Unit | H20 Evap | H20 Cond | REFR. EVAP | REFR. COND
[8 empty] | MAWP | MAWP | MAWP | MAWP
020
[7 empty] | 030 | 333 | 300 | - | 600
[7 empty] | 045 | 333 | 180 | - | 650
[7 empty] | 055 | 333 | 180 | - | 650
[7 empty] | 065 | 333 | 180 | - | 650
[7 empty] | 075 | 333 | 180 | - | 650

## Auto Populate (ACCA)
5kA OR 100kA?
5
Water Pressure?
[17 empty] | Date Manufactured | 2021-11-29 |  |  | 150
[17 empty] | Serial | 5076A-01
Model | ACC | S - Stand Alone | 070 | F - 460-3-60 | A - Air-Cooled Chiller | F - Circuit A - Tandem Compressors; Circuit B - Tandem Compressors | 0 - R-410A | 0 - Standard Efficiency | 0 - Factory Assigned | 0 - Brazed Plate | 0 - Standard Cooling 40 to 65°F [4.4 to 18.3°C] | 0 - No Valve | 0 - Microchannel Heat Exchanger (MCHE) | 1 - Variable Speed | 0 - No Heat Recovery | 0 - None
Refrigerant |  | 410A | [10 empty] | Charge | Crt 1=15.5 |  |  |  |  | Crt 2=15.5
Oil Type |  | POE | [10 empty] | Unit Weight | 2000 lbs
Maximum Operating Pressures (PSIG):
Water Side: |  |  |  |  | N/A |  |  |  | Condenser | [7 empty] | 150 |  |  | Chiller
Refr. Side: |  |  |  |  | 650 |  |  |  | Condenser | [7 empty] | 650 |  |  | Chiller
Electrical Data:
Rated | 460 |  |  |  |  | Volts |  |  |  | 3 |  |  | Ph |  |  | 60 |  |  |  | Hz
Model
Comp. #1 |  | CKT 1 |  | DSH184A4 | [5 empty] | 197 |  |  | RLA |  |  | 24.7 |  |  |  | LRA
Comp. #3 |  |  |  | DSH184A4 | [5 empty] | 197 |  |  | RLA |  |  | 24.7 |  |  |  | LRA
Comp. #2 |  | CKT 2 |  | DSH240A4 | [5 empty] | 215 |  |  | RLA |  |  | 32.7 |  |  |  | LRA
Comp. #4 |  |  |  | DSH240A4 | [5 empty] | 215 |  |  | RLA |  |  | 32.7 |  |  |  | LRA
Minimum Circuit Ampacity | [16 empty] | 142.975 |  |  | Amps
Maximum Fuse Size | [16 empty] | 175 |  |  | Amps
Recommended Dual-Element, | [16 empty] | 150 |  |  | Amps
Time-Delay Fuse Size
Fan FLA Ea. | [16 empty] | 5 |  |  | Amps
Control Panel SCCR | [16 empty] | 5 |  |  | kA RMS
(RMS Symmetrical)
Maximum Utilization Range | [15 empty] | 506 |  |  |  | Volts
Rev 0

## ACCA Look Up Tables
| ACCA Model String Selection | [12 empty] | Digit 8 |  |  | Digit 11 | Digit 12 |  |  |  |  | Digit 17 | Digit 18 - Condenser | Digit 19 - Condenser Water | Digit 20 — Heat Recovery |  |  |  |  | Digit 25 | Digit 26 -Remote BMS Interface
Digit 4 | Model = | S - Stand Alone | SELECTED UNIT | Unit Type | Unit Size | Voltage (Name Plate) | Unit MCA | Max Fuse Calc | Unit Max Fuse | Rec Fuse Calc | Unit Rec. Fuse | Unit Series | Tons | Unit Voltage | Digit 9 - Application | Digit 10 - Steps of Capacity | Refrigerant Type | Unit Efficiency | Digit 13 - Design Sequence | Digit 14 - Evaporator Heat Exchanger Type | Digit 15 — Evaporator Temp Range | Digit 16 - Evaporator Valves | Air-Cooled Condenser Heat Exchanger Type | Fan Control | Heat Recovery | Condenser Control Valves | Digit 21 — Power Connection | Digit 22 - Power Feed | Digit 23 - Service Options | Digit 24 - Control Style | Local Unit Controller Interface | (Digital Comm) | Digit 27 - Blank
Digit 5 to 7 | Nominal Capacity = | 070 |  | ACCS - Stand Alone | 070 | 460/3/60 | 142.975 | 175.675 | 175 | 159.325 | 150 | S - Stand Alone | 010 | A - 208-3-60 | A - Air-Cooled Chiller | 0 - No Compressors - Condenser | 0 - R-410A | 0 - Standard Efficiency | 0 - Factory Assigned | 0 - Brazed Plate | 0 - Standard Cooling 40 to 65°F [4.4 to 18.3°C] | 0 - No Valve | 0 - Microchannel Heat Exchanger (MCHE) | 0 - Fixed Speed | 0 - No Heat Recovery | 0 - None | 0 - Terminal Block | 0 - 5 kA Rating | 0 - None | 0 - Non-Array, Single Unit Controller | 0 - Keypad with Dot Pixel Display | 0 - None | 0 - Blank
Digit 8 | Unit Voltage = | F - 460-3-60 | [9 empty] | M - Modular | 015 | B - 230-3-60 | B - Air-Cooled Chiller (Low Ambient) | A - Single Circuit - On/Off Compressor | 2 - R-32, R-454B, R-452B, etc. | 1 - High Efficiency |  | 1 - Shell and Tube | 1 - Standard Cooling/Ice Making 15 to 65°F [-9.4 to 18.3°C] | 1 - Constant Flow Array - Manual Balancing/Isolating Valve | A - Fin and Tube | 1 - Variable Speed | 1 - Full Heat Recovery | 1 - Manual balancing/isolating valves | A - Non-Fused Disconnect Switch | A - 5 kA Rating + Phase and Voltage Monitor | A - LED Lighted Control Cabinet | A - Master Controller w/ Single Controller per Array | A - 10.1" Color Touchscreen | 2 - Lon Talk®
Digit 9 | Unit Application = | A - Air-Cooled Chiller | Note |  |  | Circuit Type | Comp Name | Comp Capacity | Comp Model | LRA | RLA | R - Remote Condenser | 020 | F - 460-3-60 | C - Air-Cooled Chiller (High Ambient) | B - Single Circuit - Tandem Compressors |  | 2 - Premium Efficiency |  | 2 - High Capacity Brazed Plate |  | 2 - Variable Flow Array - Motorized Isolating valve | B - Copper Tube, Copper Fin | 2 - Low Sound |  | 2 - Motorized Isolating valve | B - Fused Disconnect Switch | B - 100 kA Rating | B - Factory Wired 115V Outlet | B - Supervisor Array Controller w/ Controller per Module | B - 15.4" Color Touchscreen | 4 - BACnet® MS/TP
Digit 10 | Steps of Capacity = | F - Circuit A - Tandem Compressors; Circuit B - Tandem Compressors | These are array formulas, you must press CTRL+Shift+Enter |  | Circuit 1 | Tandem | Comp. #1 | DSH184A | DSH184A4 | 197 | 24.7 | U - Condensing Unit | 025 | G - 575-3-60 | D - Heat Pump | C- Single Circuit - Variable Speed Compressor |  |  |  | 3 - High Capacity Shell and Tube |  |  | C - E-Coat Microchannel Heat Exchanger (MCHE) | 3 - Ultra Low Sound |  |  | C - High SCCR Fuse Block | C - 100 kA Rating + Phase and Voltage Monitor | C - Field Wired 115V Outlet | C - Slave Expansion Board Module |  | 5 - BACnet IP
Digit 11 | Refrigerant Type = | 0 - R-410A |  |  |  |  | Comp. #3 | DSH184A | DSH184A4 | 197 | 24.7 |  | 030 |  | E - Heating Optimized Chiller | D - Circuit A - On/Off Compressor; Circuit B - On/Off Compressor |  |  |  | 4 - Coaxial |  |  | E - E-Coat Fin and Tube |  |  |  | D - Distribution Panel for Array |  | D - LED Lighted Control Cabinet + Factory Wired 115V Outlet |  |  | 6 - MODBUS®
Digit 12 | Unit Efficiencty = | 0 - Standard Efficiency |  |  | Circuit 2 | Tandem | Comp. #2 | DSH240A | DSH240A4 | 215 | 32.7 |  | 040 |  |  | E - Circuit A - Tandem Compressors; Circuit B - On/Off Compressor |  |  |  | 5 -Flooded Barrel |  |  | F - E-Coat Copper tube, Copper Fin |  |  |  | E - Circuit Breaker with High Fault Rating |  | E - LED Lighted Control Cabinet + Field Wired 115V Outlet |  |  | 8 - Johnson N2
Digit 13 | Design Sequence = | 0 - Factory Assigned |  |  |  |  | Comp. #4 | DSH240A | DSH240A4 | 215 | 32.7 |  | 050 |  |  | F - Circuit A - Tandem Compressors; Circuit B - Tandem Compressors |  |  |  | 6 - Remote Brazed Plate
Digit 14 | Evap Type = | 0 - Brazed Plate | Look Up Values | [9 empty] | 060 |  |  | G - Circuit A - Variable Speed; Circuit B - On/Off Compressor |  |  |  | 7 - Remote Shell and Tube
Digit 15 | Evap Temp Range = | 0 - Standard Cooling 40 to 65°F [4.4 to 18.3°C] | ACCS - Stand Alone | [9 empty] | 070 |  |  | H - Circuit A - Variable Speed; Circuit B - Tandem Compressors |  |  |  | 8 - Remote High Capacity Brazed Plate
Digit 16 | Evap Valves = | 0 - No Valve | 070 |  | Capacity | Compressor Tyle | Compressor |  |  | Unit Fans | Fan FLA |  | 080 |  |  | J - Circuit A - Variable Speed; Circuit B - Variable Speed |  |  |  | 9 - Remote High Capacity Shell and Tube
Digit 17 | Condenser Type = | 0 - Microchannel Heat Exchanger (MCHE) | F - 460-3-60 |  | 010 | Single Single | DSH120A |  |  | 4 | 5
Digit 18 | Condenser Fans = | 1 - Variable Speed | 460 |  | 010 | Single Tandem | HLH061T
Digit 19 | Heat Recovery = | 0 - No Heat Recovery | Dual Tandem |  | 010 | Single Variable | VZH065
Digit 20 | HR Valves = | 0 - None | SE |  | 010 | Single | HLH061T |  |  | Unit | Fan Count
[5 empty] | 010 | Tandem | N/A |  |  | 010 SE | 1 | A - 208-3-60 | 200-230/3/60 | 208 | 3
[5 empty] | 010 | Variable | N/A |  |  | 015 SE | 1 | B - 230-3-60 | 200-230/3/60 | 230 | 3
[5 empty] | 015 | Single Single | DSH184A |  |  | 020 SE | 1 | F - 460-3-60 | 460/3/60 | 460 | 4
[5 empty] | 015 | Single Tandem | DSH090A |  |  | 025 SE | 1 | G - 575-3-60 | 575/3/60 | 575 | 7
[5 empty] | 015 | Single Variable | VZH088 |  |  | 025 HE | 2
[5 empty] | 015 | Single | DSH090A |  |  | 030 SE | 1 | A - Single Circuit - On/Off Compressor | Single On/Off
[5 empty] | 015 | Tandem | N/A |  |  | 030 HE | 2 | B - Single Circuit - Tandem Compressors | Single Tandem
[5 empty] | 015 | Variable | N/A |  |  | 040 SE | 2 | C- Single Circuit - Variable Speed Compressor | Single Variable
[5 empty] | 020 | Single Single | DSH240A |  |  | 050 SE | 2 | D - Circuit A - On/Off Compressor; Circuit B - On/Off Compressor | Dual Single
[5 empty] | 020 | Single Tandem | DSH120A |  |  | 050 HE | 2 | E - Circuit A - Tandem Compressors; Circuit B - On/Off Compressor | Tandem/Single
[5 empty] | 020 | Single Variable | VZH117 |  |  | 060 SE | 2 | F - Circuit A - Tandem Compressors; Circuit B - Tandem Compressors | Dual Tandem
[5 empty] | 020 | Single | DSH120A |  |  | 060 HE | 4 | G - Circuit A - Variable Speed; Circuit B - On/Off Compressor | Variable/Single
[5 empty] | 020 | Tandem | N/A |  |  | 070 SE | 4 | H - Circuit A - Variable Speed; Circuit B - Tandem Compressors | Variable/Tandem
[5 empty] | 020 | Variable | VZH065 |  |  | 080 SE | 4 | J - Circuit A - Variable Speed; Circuit B - Variable Speed | Dual Variable
[5 empty] | 025 | Single | DSH140A
[5 empty] | 025 | Tandem | N/A
[5 empty] | 025 | Variable | ZVH088
[5 empty] | 030 | Single | DSH184A
[5 empty] | 030 | Tandem | DSH090A
[5 empty] | 030 | Variable | VZH117
[5 empty] | 040 | Single | DSH240A
[5 empty] | 040 | Tandem | DSH120A
[5 empty] | 040 | Variable | VZH170
[5 empty] | 050 | Single | DSH295A
[5 empty] | 050 | Tandem | DSH140A
[5 empty] | 050 | Variable | VZH170
[5 empty] | 060 | Single | DSH381A
[5 empty] | 060 | Tandem | DSH184A
[5 empty] | 060 | Variable | N/A
[5 empty] | 070 | Single | DSH381A | DSH485A
[5 empty] | 070 | Tandem | DSH184A | DSH240A
[5 empty] | 070 | Variable | N/A | N/A
[5 empty] | 080 | Single | DSH485A
[5 empty] | 080 | Tandem | DSH240A
[5 empty] | 080 | Variable | N/A

## Sheet1
Compressor Model | Compressor LRA | Compressor RLA | Industry Standard sizes for Fuses
DSH090A3 | 203 | 27.5641 | 1
DSH090A4 | 98 | 14.1026 | 3
DSH090A7 | 84 | 11.5385 | 6
DSH120A3 | 267 | 39.1026 | 10
DSH120A4 | 142 | 18.5897 | 15
DSH120A7 | 103 | 15.3846 | 20
DSH140A3 | 304 | 41.0256 | 25
DSH140A4 | 147 | 19.2308 | 30
DSH140A7 | 122 | 16.6667 | 35
DSH184A3 | 351 | 48.0769 | 40
DSH184A4 | 197 | 24.7436 | 45
DSH184A7 | 135 | 22.4359 | 50
DSH240A3 | 485 | 67.3077 | 60
DSH240A4 | 215 | 32.6923 | 70
DSH240A7 | 175 | 26.2821 | 80
DSH295A3 | 560 | 82.0513 | 90
DSH295A4 | 260 | 39.7436 | 100
DSH295A7 | 210 | 28.8462 | 110
DSH381A3 | 717 | 108.9744 | 125
DSH381A4 | 320 | 50.641 | 150
DSH381A7 | 235 | 38.4615 | 175
DSH485A3 | 1010 | 121.7949 | 200
DSH485A4 | 344 | 67.9487 | 225
DSH485A7 | 327 | 45.5128 | 250
VZH088-J |  | 74.8 | 300
VZH088-G |  | 37.5 | 350
VZH088-H |  | 37.5 | 400
VZH117-J |  | 88 | 450
VZH117-G |  | 44 | 500
VZH117-H |  | 44 | 600
HLH061T2 | 170 | 19.2308 | 700
HLH061T4 | 82 | 9.6154 | 800
VZH170-J |  | 115 | 1000
VZH170-G |  | 61 | 1200
VZH170-H |  | 61 | 1600
2000
2500
3000
4000
5000
6000